## New Wateryard (hidden)
BILL OF QUANTITIES
South Sudan Enhancing Community Resilience and Local Governance Project (ECRP)
Project Description: Wungok Village GPS : N=10.07358889, E=29.89319444 (Wungok Boma)-Werthen Payam, Abouny Village GPS: N=9.939001, E=29.825724 (Wunkur Boma)-Aliiny Payam ; Ayija Village GPS: N=9.88216667, E=29.94313889 (Akotweng Boma)-Nyiel Payam; Drilling and construction of 3 new water yards installed with solar panels and submersible pump;
Name of Bidder:
I | Description | Unit | Quantity required for project | Unit Cost [USD] | Total cost (USD)
BILL NO 1 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT |  |  |  | 0
1 | SOLAR SYSTEM
1.1 | Supply and installtion of a Dayliff or Lorentz solar system providing at least 36m3/day considering 6 hours of sunshine. The system shall comprise of a submersible pump and well probe, float switch, smart PSU with wireless data connect, PV Disconnect, surge protector and lighting arrestor with a minimum of 1 piece of 8‐foot copper‐plated grounding rod. Design of the solar system needs to be inspected and validated by IOM prior to procurement and installation. | LS | 1 |  | 0
2.1 | Supply and install of a parallel series solar pannels certified to ISO, IEC 61215 and 61730 (TÜV Rheinland) and CE oversized by 1.2 to 1.3 times the motor size. The solar panels shall be mounted facing North and a tilt angle of 7deg, mounted onto a fabricated frame above the storage tanks. | LS | 1 |  | 0
3 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT
3.1 | Horizontal installation of 3 flow meters, at the inlet of the storage, and 1 per water kiosk. | pcs | 3 |  | 0
3.2 | Supply and installation of 6.0 metre high metalic stand tower for tank, evenly coated with a layer of anti-oxide paint and overlayed with an additional coating of grey/silver paint and fitted with a hooped cat-ladder, top walkways of 2.1mm thickness and safety hand railings. Tower to comply to manufacturing standards: Dead/Live load analysis to BS 6399. Wind load analysis to CP3 ch V 1972. Structural steel work to BS 5950 Part 1 1990. | LS | 1 |  | 0
3.3 | Supply and installation of 2 PVC high quality water tank of 5,000 liter each (Toptank recommended). | pcs | 2 |  | 0
3.4 | Supply and installation of 2-1/2'' HDPE underground distribution and uPVC, PPR class 10 above ground pipeline and fittings. | m | 300 |  | 0
4 | WATER YARD SITE LAYOUT
4.1 | The borehole shall be fitted with a well head casted in a concrete platform of minimum 0.3m height and protected by a man hole with a cast iron trap fitted with a lockable system. | LS | 1 |  | 0
4.2 | Levelling of the site and laying a 300mm thickness well compacted murram of 60% minimum aggregate approved by the IOM Supervisor prior to installation. | LS | 1 |  | 0
5 | REPORTING
5.1 | Submit well completion report as per IOM template, including results of water quality analysis. | No | 1 |  | 0
BILL SUMMARY
BILL NO 1 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT | Unit | 3 | 0 | 0
|  | GRAND TOTAL |  |  | 0

## Water Yard Rehabilitation (hidden)
BILL OF QUANTITIES
South Sudan Enhancing Community Resilience and Local Governance Project (ECRP)
Project Description: Abon 2 Village GPS: N=9.918025, E=29.98141389 (Waukok Boma)-Pariang Payam, - Drilling and rehabilitation of existing water yard installed with solar panels and submersible pump, Pariang County, Unity State
Name of Bidder:
I | Description | Unit | Quantity | Unit Cost | Total cost
BILL NO. 1 | PRELIMINARIES |  |  |  | 0
Notes:
| All the Bidders are requested to refer "Pricing Preamble and notes below" and works items of this Bills of Quantities shall be priced to fulfill the requirements there-in. Also see that no page or items are missing prior to pricing of this bill of quantities. | Note
| A list of typical general items are given below. However, the Bidder is requested to price only those items that may affect this Contract. | Note
| If no price has been stated against any item hereunder, the Contractor shall not be entitled to claim any money for such items even though he is obliged to execute the work or provide services described therein. Preliminary items priced by the Tenderer are deemed to include the cost of unpriced items. | Note
| Cost and expenses in connection with any other preliminary item which is not listed below, but is necessary for the due completion of works, is deemed to be included in the tender rates. | Note
1.1 | Site Facilities |  |  |  | 0
1.1.1 | Mobilization and demobilization from the site including all requirements of Guideline GHS12 - Site Establishment - Preparation works, protection of existing structures, materials and items, site boundaries, information board, office and welfare facilities, storage sites, generator, site reinstatement, safety, and security | 1 | Lump Sum |  | 0
1.1.2 | Fabricate a metal visibility plate 100 x 80 mm to be wall mounted. Art work of name board will be issued by IOM | 1 | each |  | 0
1.2 | Sites Operations |  |  |  | 0
1.2.1 | Allow for setting out of works in accordance with drawings; liaise with client to establish exact boundaries and other written information given by the Engineer and obtain written approval from the relevant government authorities for setting out, street and building lines before commencements of construction; Checking of any setting out or of any line or level by the Engineer shall not in any way relieve the Contractor of his responsibility for the accuracy thereof. | 1 | Lump Sum |  | 0
1.2.2 | Tools, plant, and scaffolding | 1 | Lump Sum |  | 0
1.2.3 | Allow for providing all necessary safety measures to workmen (provision for proper usage of Personal protective equipment (PPE)). | 1 | Lump Sum |  | 0
1.3 | Insurances, Bonds & Fees |  |  |  | 0
1.3.1 | Allow for Contractor's All Risk Insurance Policy, including third party liability and from the starting date until the defects liability certificate has been issued, the risks of personal injury, death, and loss of or damage to property (including, without limitation, the works, plant, materials, and equipment) which are not employers risk but are contractors risk Allow for insurance against claims for worker's compensation. Engineer's and Consultant's representatives, shall be included in the Insurance Policy. Allow for insurance against loss or damage to the works, adjacent structures, any existing overhead and/or underground services that may cause damages during the construction | 1 | Lump Sum |  | 0
BILL NO. 4 | REHABILITATION OF EXISITING WATER YARD |  |  |  | 0
4.1 | Supply and Installation of solar pump, solar panels and accessories | Unit | Quantity | Unit Rate | 0
4.1.1 | Supply and install Deep Well Submersible Pump, 4" 2 HP, 220V, 35 GPM, 400 ft Max, long life, to provide at least 48m3/day considering 8 hours of sunshine and a total dynamic head of 90m. The system shall comprise of control panel, submersible cable of at least 110m, float switch, UPVC Riser pipes and adaptor set, surge protector and lighting arrestor with a minimum of 1 piece of 8‐foot copper‐plated grounding rod. Design of the solar system needs to be inspected and validated by IOM prior to procurement and installation. | LS | 1 |  | 0
4.1.2 | Supply and install in a parallel series solar pannels 300 W and above, certified to ISO, IEC 61215 and 61730 (TÜV Rheinland) and CE oversized by 1.2 to 1.3 times the motor size. The solar panels shall be mounted facing North and a tilt angle of 7deg, mounted onto a fabricated frame above the storage tanks. | LS | 1 |  | 0
4.2 | Water tank rehabilitation, Water distribution network and rehabilitation of existing water points. |  |  |  | 0
4.2.1 | Horizontal installation of 4 flow meters, at the inlet of the storage, and 1 per water stand tap station | pcs | 4 |  | 0
4.2.2 | Repair and modify the existing 6.6 metre high metalic stand tower, including providing metallic solar panels carrier welded to the existing stand tower at least 1m above water tank, ensuring strong bracings and all necessary support to resist effect of wind force. Ensure that the solar panel carrier is inclined and oriented appropariately. Conduct thorough check on the exisiting 20M3 metallic circular tank against any leakage, evenly coated with a layer of anti-oxide zinc phosphate paint and overlayed with an additional coating of grey/silver paint and fitted with a hooped cat-ladder, top walkways of 2.1mm thickness and safety hand railings. | LS | 1 |  | 0
4.2.3 | Supply and installation of 2-11/2'' HDPE underground distribution and uPVC, PPR class 10 above ground pipeline and fittings. | m | 400 |  | 0
4.2.4 | Rehabilitation of 4 water points with 3 Talbot Talflow self closing taps each in hollow block and concrete masonry including construction of a drainage channel and a soak away pit. | pcs | 4 |  | 0
4.3 | SITE LAYOUT |  |  |  | 0
4.3.1 | The borehole shall be fitted with a pedestal stand casted raised at least 0.7m in a concrete platform of minimum 0.3m thick and protected by a man hole with a cast iron trap fitted with a lockable system. The well must have provision for deep meter hole to check static water level and depth of BH | LS | 1 |  | 0
4.3.2 | Levelling of the site and laying with well compacted murram of 60% minimum aggregate laid at interval not exceeding 100mm thick until 300mm thickness is achieved, as approved by the IOM Supervisor prior to installation. | LS | 1 |  | 0
4.3.3 | Supply and installation of a fence 8m x 8m to secure the solar system and the borehole (if feasible). The fence shall be constructed using Y shaped circular steel hollow section tubes of 50mm diameter by 3mm thickness or casted in a concrete (1:2:4) foundation (W: 0.3 X L: 0.3 X H: 0.7 m). The top part of the pole shall be welded with V-shaped of 500mm length and installed with razor wire of 0.9m diameter. The height of the pole above ground shall be determined by the height of the chain link supplied but should be of minimum 1.9m. The poles shall be installed 1.5 meters apart and reinforced using 3 lines of tension wire. An apron of 200mm wide shall be casted all round along the fence perimeter | LS | 1 |  | 0
4.3.4 | Installation of a gate frame constructed with 2 pieces of 100mm x 100mm x 3mm (4x4 inch) hollow section frame, each supported by an additional member placed at 60deg angle from the vertical pole. The gate itself shall be constructed with 60mm x 60mm x 3mm hollow sections shutter frame and covered with wire mesh. | LS | 1 |  | 0
4.3.5 | Fence and gate shall be evenly painted with a single layer of anti-oxyde paint and overlayed with an additional coating of grey/silver paint. | LS | 1 |  | 0
4.3.6 | Supply and installation of 2 modular all-in-one solar street lights, attached directly onto the solar frames and secured by razor wire. | pcs | 2 |  | 0
BILL SUMMARY
BILL NO. 4 | REHABILITATION OF EXISITING WATER YARD | Unit | 1 | 0 | 0
|  | GRAND TOTAL |  |  | 0

## Bill No. A-MILK
BoQs FOR SOLAR POWERED MILK COOLING FRIDGE AND MILK CONTAINERS 20 LITER CAPACITY , MSME. - JALAM - BURTNLE DISTRICT-PUNTLAND
BoQs of MILK PROCESSING [SOLARIZATION MILK] Solar powered milk cooling fridge for small holder women milk street vendors. - Jalam- Burtinle-Puntland
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | BoQs of Supply and Installation of ] (BoQs for Solar powered milk cooling for Enhance the availability of both on-grid and off-grid renewable energy solutions for households and Micro, Small, and Medium Enterprises (MSMEs )
A 1 | The refrigerator is required to mechanically and compatibly source power from the following specifications of electric supplying solar, that is also associated with energy storage battery. In other words, each refrigerator is accompanied by one (1) unit of below solar system: (The cost of anchorage of all the solar panels is inclusive.)
1 | • Temperature: 15~ -18℃ • Refrigerant: R134a • Capacity: 358L • Color: Silver • Style: Chest Deep • Power Source: Solar DC battery, Battery, Solar • Input voltage: 12V 24V • Solar panel: Class A Mono • Door: Single Folding • Temperature Type: Single-Temperature • After-sales Service Provided: Free spare parts • Warranty: 5 years • Operating Language: English • Application: Outdoor, garage, Commercial, Household, Hotel • App-Controlled: NO • Private Mold: Yes • Logo/Pattern: Silk screen printing • Brand Name: Quality motivated • Model Number: 2024 and after • Application: Commercial outdoor (street milk business) • Climate type: Arid and semi-arid lands (ASAL). Resilient to hot weather like the one for Somalia, shockproof and durable for handling in rough road. • Digital display with individual temperature control: LED display touch control panel makes temperature adjustment easy (if possible). • Free spare parts accompanied: Welcomed • Conformity with German/EU Standards ( CE) The refrigerator is required to mechanically and compatibly source power from the following specifications of electric supplying solar, that is also associated with energy storage battery. In other words, each refrigerator is accompanied by one (1) unit of below solar system: (Cost is inclusive of anchorage and support at the roof of the cold storage & dispatch structure) •Solar Cell: Monocrystalline • Surface material: ETFE • Cloth color: Black • Open size: 2510 × 1100mm • Net weight 8.4 KG • Type of Connector: XT60 + Anderson + GX16 + DC • Additional design: Kickstands • Certifications: CE, FCC, ROHS, REACH • Conformity with German/ European Standards (CE ) • Standard Test Condtion: Irrandiance 1000W/㎡ • Module temperature: 25℃,AM=1.5 • Maximum power(Pm): 450W • Voltage at max power(Vmp): 18V • Current at max power(Imp): 22.2A • Open circuit voltage(Voc): 21.6V • Short circuit current(Isc): 24.2A • Temperature Coefficient of Pmax: (-0.41% /ºC) • Temperature Coefficient of Voc: (-0.33% /ºC) • Temperature Coefficient of Isc: (+0.06% /ºC) • Power Tolerance: -0%, +5% • Maximum System Voltage: 1500V DC • Maximum Series Fuse Rating: 25A • Operating Temperature: -20℃~65℃ • Noct*: 45℃ ± 2℃ • Warranty: 5 years product warranty on materials and workmanship • Power is not less than 95% in 5 years. Battery Type Deep Cycle Sealed Lead Acid (Gel or AGM) Nominal Voltage 12V DC Capacity 150Ah (can vary between 100Ah–200Ah based on load and autonomy) Energy Storage 1.8 kWh (12V × 150Ah) Design Life 5–8 years (depending on usage and ambient temperature) Charge Efficiency ≥ 95% Discharge Depth Up to 80% DoD (Depth of Discharge) Operating Temperature -10°C to +50°C Cycle Life 1000+ cycles at 50% Depth of Discharge Dimensions (L×W×H) ~ 483 × 170 × 240 mm (varies slightly by manufacturer) Weight ~ 40–45 kg (for 150Ah) Terminal Type M8 or F12 (depends on model) Certifications ISO 9001, CE, RoHS. This including all the necessary fittings and installation of the solar system | Unit | 12 |  | 0
2 | • Use for milk transportation and storage. • Capacity: 20 L. •Material Grade: Food Grade type 304 Stainless Steel. The material should have high corrosion resistance. • Should have a secured stainless steel food grade lid that should close the can tightly for safe transportation, with latch. The lid should be airtight and leak-proof to prevent contamination and maintain freshness. • Should have firmly installed, well-fitted riveted double sided wire handles for easy transportation. | Unit | 24 |  | 0
3 | Fabrication, supply, and installation of complete street vending kiosk unit – Dimensions approximately 1.5m (L) × 1.20m (W) × 2.2m (H); fabricated using 25mm × 25mm mild steel square tubes, primed and painted with anti-rust enamel paint. Includes the following integrated components: • Roofing canopy made of 1mm thick galvanized steel sheet, powder-coated or painted blue and white.• Working counter top (1.5mm thick mild steel sheet) welded and reinforced.• Two lockable lower storage compartments with sheet metal doors, hinges, handles, and padlock hasps.• Branding and labeling with project logo and identification number as directed by the site engineer. | Unit | 12 |  | 0
B.1 | Attached for Images is used for just visualising the requirement.
Total of Bill NO. A, BoQs of SOLAR POWERED MILK COOLING FRIDGE AND MILK CONTAINER 20 LITRES CAPACITY, CARRIED FORWARD TO SUMMARY |  |  |  |  | 0

## Bill No. B-COLD STORAGE UNIT(S)
BoQs FOR REHABILITATION OF A FUNCTIONAL SOLAR POWERED COLD STORAGE FACILITY , MSME.
Proposed Renovation Of Stand-alone cold storage unit for small holder women milk street vendors - JALAM.
ITEM | DESCRIPTION | QTY | UNIT | UNIT COST $ | TOTAL COST (USD)
SITE PREPARATION
Clearing site vegetation;grabbing up roots and filling up voids left with selected materials
A | Bushes ,shrubs, undergrowth or the like and cartaway from site upto depth of 300mm; cost inclusive of alignment of the area as approved by the engineer. | 120 | SM |  | 0
B | Allow lumpsump cost for all demolitions and disposals within the scope. | 1 | LumpSum |  | 0
C | Supply and install pre-approved cabinets for storage of milk quality testing machines and other milk additives and preservatives; should be made of cypress or alternative hardwood such as oak as per engineer's instructions. Each cabinet should have atleast 6 drawers which are lockable. | 2 | NO |  | 0
D | Install prepainted 225mmx15mm fascia board all round the structure cost inclusive of any truss member replacement, repair,nails for structural integrity. Must be aesthetically pleasing and aligned with zero tolerance to errors. | 50 | LM |  | 0
| Totals carried to main summary (TTS 1) |  |  |  | 0
ROOFING
ROOF COVER
Repair and or replace worn out items;
Gauge 30 box profile pre-painted Blue G.C.I roofing sheets or matching with existing roof
A | fixed to purlins (measured separately) use silicon sealant as and when necessary to mitigate leaking roofs and provide the roof truss and sheets for the latrine and worn out underground water tank cover | 60 | SM |  | 0
B | Gauge 30 pre-painted ridge cap | 10 | LM |  | 0
| Totals carried to main summary (TTS 2) |  |  |  | 0
WINDOWS & DOORS
STEEL DOORS
Standard steel panelled door in equal embossed panels framed in 25 x3mm SHS frame complete with all necessary iron mongery assembled and fixed to opening including cutting and pinning to concrete or blockwork surround and bedding frame in cement ) all primed with red oxide before fixing. The Double opening outwards.
A | Overall Max size 1600x2400mm External Single leaf door; actual size and alignment matching the existing doors. Sum to include applying three coat paint to engineer's approval: The door must open outward. | 3 | No |  | 0
| Totals carried to main summary (TTS 3) |  |  |  | 0
FINISHES
PAINTING AND DECORATING
ONE UNDERCOAT TWO COATS OIL PAINTFULL GLOSS FINISH TO CROWN PAINTS OR EQUAL AND APPROVED
A | All internal door & window surfaces over 300mm girth internal | 6 | SM |  | 0
0
CEILING
| Allow sum to install, repair,repaint, restore and replace the existing ceiling to the engineer's approval and instructions | 80 | SM |  | 0
FLOOR FINISHES
B | Supply and install non skid tiles to the floors to the engineers approval giving high quality tiles max size 600x600 and of the highest workmanship levels | 120 | SM |  | 0
WALL FINISHES
wall repair: hacking and applying plaster
C | 12mm thick cement and sand to concrete or blockwork to internal walls with a steel finish, allow for the provision of blackboard (Blackboard for duty rosters with Pre-approved well finished, chamfered timber frame) | 60 | SM |  | 0
ditto
D | to external walls and recess with a bituminous or approved glossy paint - best in the market as approved | 100 | SM |  | 0
PAINTING & DECORATING
The color coding for sections will vary thereby the contractor is advised to get instructions before any works.
ONE UNDERCOAT AND 3 COATS OF PLASTIC EMULSION PAINT (SILK VINYL) TO CROWN PAINTS OR EQUAL AND APPROVED
E | Supply and apply approved quality undercoat and 3 coats of soft white Emulsion paint of Specific color as will be instructed, (quality crown super premium grade silk vinyl matt soft-white). | 260 | SM |  | 0
F | Ditto but approved EU blue colour gloss paint for external columns for the verandah | 3 | NO |  | 0
H | Allow sum for Organization and specific donor Branding as approved/Instructed by the UN preferable at one side of the gable walls or the front elevation of the structure. | 1 | LumpSum |  | 0
I | Allow cost of professional graphic and text artistic public awareness campaign painting and message for internal and external walls | 24 | SM |  | 0
| Totals carried to main summary (TTS 4) |  |  |  | 0
ELECTRICAL WORKS : SOLARIZATION
All accessories, machines and solar equipment must have the manufacturing country in EU unless allowed by the engineer. They must have a warranty of not less than 1 year.
The proposed system must be clearly attached as part of the deliverables in the bid documents stating the sytem and make of the deliverables, giving a justification for your lumpsum.
A | Allow a sum to boost the additional energy: requirements to include fittings and installations including casing of cables along the walls and making good the surfaces after, conduit fitting, cabling, switches, sockets and internal light fittings. Provide and install upto One security lights;( Solar Lights that is outdoor Waterproof with Motion Sensor Flood Outside Lights with 2500LM High Brightness 270° Wide Angle, Outdoor Solar Lights IP65). The scope includes testing to ensure its workability. (Allow sum for additional solar panels in addition to the ones procured under bill A for a working solar powered system) | 1 | Lumpsum |  | 0
B | Allow a sum for a complete repair of the existing plumbing fittings and installations including all repairs, replacement and all the necessary plumbing accessories; Scope to include supply and installation of two new double sinks made of stainless steel which will be positioned outside the facility and pre-approved by the engineer. | 1 | Lumpsum |  | 0
C | Supply and offer basic training of 4 women/youth (User Manual) on the use of a pre-approved portable milk quality analyzing machine(s) from a reputable EU brand preferred: The machine must be simple to use, affordable, and measure basic milk quality checks such as ph, temperature, fats etc. | 1 | NO |  | 0
D | Allow sum to provide a pre-approved standard solar battery storage metallic cage, well raised and anchored within the cold storage unit with dimensions of upto 1.5m long and 0.6m long; Include timber stands to hold the supplied refrigerators from direct contact with the floor. | 1 | LS |  | 0
| Totals carried to main summary (TTS 5) |  |  |  | 0
GRAND SUMMARY
| TTS 01 |  |  |  | 0
| TTS 02 |  |  |  | 0
| TTS 03 |  |  |  | 0
| TTS 04 |  |  |  | 0
| TTS 05 |  |  |  | 0
| GRAND TOTAL FOR COLD STORAGE UNIT |  |  |  | 0

## Summary
PRICED BoQs FOR SOLAR POWERED MILK COOLING FRIDGE, REHABILITATION OF COLD STORAGE FACILITY AND MILK CONTAINER 20 LITRE CAPACITY , MSME.
Summary Ref:PRN
ITEM | DESCRIPTIONS | Unit | Quantity required | Total cost for Bill NO. | Overall Total cost (USD)
1 | Total of Bill NO. BoQs of SOLAR POWERED MILK COOLING FRIDGE AND SOLAR CELL. | Milk cooling Fridge | 12
2 | MILK TRANSPORTATION AND MILK CONTAINER 20 LITTER CAPACITY | Transportation milk container 20L | 24 CONTAINERS
3 | FABRICATION, SUPPLY AND INSTALLATION OF COMPLETE STREET VENDING KIOSK UNIT. | street vending kiosk unit | 12
4 | REHABILITATION OF COLD STORAGE FACILITY | STORAGE FACILITY | 1
Grand Total of Summary- USD $ |  |  |  |  | 0
Important Note: